## Integrator checklist
Tensor Cloud battery optimization - Integrator checklist (spec revision 2.9.0, wire schema_version 2.9.0)
Fill in the Result column with PASS, FAIL, N/A, or leave blank for not-yet-run. Use Notes for follow-ups. Before you start, the EMS you test with (physical or virtual) must be sending telemetry: Tensor Cloud only publishes commands to a gateway it sees reporting, so items that depend on receiving a command stay blocked until telemetry is flowing and the battery is registered and associated with your gateway. Online reference: https://docs.tensorenergy.jp/guides/ems-integration/integrator-checklist
88 test items below. Test IDs are stable identifiers carried across revisions, so they are deliberately not consecutive - no rows are missing. Items whose Verification column reads "Integrator test" depend on receiving an invalid or rejected command, which Tensor Cloud never sends, so they cannot be reproduced against a live connection - cover them with your own unit or integration tests against a mocked MQTT broker.
Module | Test ID | Test name | Description | Pass criteria | Applies to | Verification | Result | Notes
Connection | C-1 | TLS to broker endpoint | Open a TLS connection to the documented broker hostname on port 8883. Validate the server certificate against the Tensor Cloud CA chain. | Connection established, server certificate verified, plaintext on :1883 refused. | All | Live
Connection | C-2 | Per-gateway certificate uniqueness | Confirm each gateway is provisioned with its own client certificate. Attempt a second concurrent connection using the same certificate from a different host. AWS IoT Core disconnects the older session. | Each gateway has a unique certificate; opening a second concurrent connection with the same certificate disconnects the first. | All | Live
Connection | C-3 | CA chain validation | EMS validates the broker certificate against the documented CA chain. Reject connections when the chain is broken or expired. | Invalid or self-signed broker certificate is rejected. | All | Live
Connection | C-7 | QoS and application-level acknowledgement | The EMS uses MQTT QoS 0 or 1 as appropriate; both are supported by the broker. Regardless of QoS, the EMS sends an application-level CommandResponse on ack-cmd/{siteId} for every command received, since it carries validation results, not delivery confirmation. | EMS publishes at QoS 0 or 1; EMS sends an application-level CommandResponse for every command received, independent of the MQTT QoS in use. | All | Live
Connection | C-8 | Reconnect with backoff | After a broker disconnect, the EMS reconnects with an exponential or otherwise capped backoff policy. | Reconnect storms avoided; subscriptions re-established before resuming publishes. | All | Live
Connection | C-9 | Behavior when telemetry cannot be published | When the EMS cannot publish (broker unreachable, TLS error), it buffers telemetry locally rather than dropping it silently. | Buffered telemetry replays per the Backfill module (see BF-1). | All | Live
Topic addressing | T-1 | siteId format | Site identifiers are prefixed si_ followed by six lowercase alphanumeric characters (e.g. si_qcf9gn). | Every siteId used in publish or subscribe topics matches ^si_[a-z0-9]{6}$. | All | Live
Topic addressing | T-2 | gatewayId format | Gateway identifiers are prefixed gw_ followed by six lowercase alphanumeric characters. | Every gatewayId matches ^gw_[a-z0-9]{6}$. | All | Live
Topic addressing | T-3 | Publish topic patterns per channel | EMS publishes only on the schema-defined topics: dt/{siteId}/{gatewayId}/{metric}/{lifetime¦energy/{window}¦power¦state}, dt/{siteId}/{gatewayId}/{curtailment¦irradiation¦alert¦alert/active¦frequency}, ack-cmd/{siteId}. | No publishes to topics outside this list. | All | Live
Topic addressing | T-4 | Subscribe topic patterns per channel | EMS subscribes only to cmd/{siteId}/battery/power, cmd/{siteId}/battery/fcr (FCR integrators only), and ack-dt/{siteId}/{gatewayId}. Wildcards permitted as alternative. | Documented subscriptions match the list above. | All | Live
Topic addressing | T-5 | res_topic namespace | res_topic on every received command points back to the same site. AWS IoT Core enforces topic scoping at the broker layer. | Publish to res_topic succeeds for legitimate commands; foreign-site attempts rejected by broker. | All | Live
Topic addressing | T-6 | ack-cmd and ack-dt namespaces | Command responses are published on ack-cmd/{siteId}. Telemetry feedback is received on ack-dt/{siteId}/{gatewayId}. | EMS uses the correct namespace for each direction. | All | Live
Topic addressing | T-7 | ack-dt topic shape | Telemetry feedback arrives on ack-dt/{siteId}/{gatewayId} exactly. No /telemetry suffix. | EMS subscribes to ack-dt/{siteId}/{gatewayId}. | All | Live
Topic addressing | T-8 | Hot-standby acknowledgement | In hot-standby, only the active gateway acks commands and executes schedules. The standby gateway is subscribed but stays silent until promoted. Primary/standby coordination is the EMS partner's responsibility. | Under hot-standby, exactly one CommandResponse per command, and exactly one gateway executes the schedule. | All | Live
Message envelope | E-1 | schema_version present on every message | Every published payload includes schema_version, including AlertEvent and AlertState. | schema_version present on every message the EMS emits. | All | Live
Message envelope | E-2 | schema_version value | schema_version is "2.9.0" for every message emitted under spec revision 2.9.0. A patch revision of the spec does not change the wire value, so the two can differ between releases. Tensor Cloud remains backwards-compatible with older revisions. | Every emitted schema_version is "2.9.0". | All | Live
Message envelope | E-3 | message_id format | Every message_id matches ^msg_[0-9a-f]{8}-[0-9a-f]{4}-[0-9a-f]{4}-[0-9a-f]{4}-[0-9a-f]{12}$. | All generated message_id values pass the regex. | All | Live
Message envelope | E-4 | command_id correlation | Every CommandResponse carries command_id equal to the originating command's message_id. Exception: an unparseable command (MESSAGE_MALFORMED) has no recoverable message_id, so the response carries the sentinel command_id "unknown". | Every response's command_id matches a command's message_id; for a deliberately malformed (non-JSON) command, the response carries command_id "unknown". | All | Live + integrator test
Message envelope | E-5 | Timestamps | All *_ts fields are ISO-8601 timestamps with a timezone offset (e.g. 2024-01-05T00:00:00.000+09:00). | Every emitted timestamp parses as ISO-8601 with offset. | All | Live
Message envelope | E-6 | additionalProperties policy | Schema allows unknown fields on every message family for forward-compatibility. EMS still emits only schema-defined fields; receivers tolerate additions. | Every emitted payload contains only schema-defined fields. Parser tolerates unknown fields without crashing. | All | Live
Message envelope | E-7 | measurement_ts alignment | On measurements covering a period, measurement_ts carries the start of that period, never its end or midpoint: windowed energy equals measurement_value.start_ts; power or frequency sent with aggregation: average is the start of aggregation_window. Point-in-time telemetry is the instant measured. Curtailment, a schedule rather than a measurement, is the TSO-issued schedule creation time when available, otherwise the time the EMS received it from the TSO. | Every windowed energy payload has measurement_ts equal to its start_ts; every aggregation: average power or frequency payload has measurement_ts at the start of its aggregation_window; curtailment measurement_ts reflects TSO schedule creation or receipt time. | All | Live
Message envelope | E-8 | Curtailment interval alignment | Every interval in a Curtailment payload is one 30-minute slot: start_ts and end_ts land on minute 00 or 30 in JST with zero seconds, and end_ts is exactly 30 minutes after start_ts. A curtailment covering a longer period is published as consecutive 30-minute intervals rather than one long interval. An interval that breaks either rule is rejected with TIME_WINDOW_INVALID. | Every published curtailment interval starts and ends on a 30-minute boundary and spans exactly 30 minutes; a curtailment running 14:00 to 16:00 is published as four consecutive intervals. | All | Live
Battery telemetry | BT-1 | Power telemetry shape | Battery power telemetry publishes on dt/{siteId}/{gatewayId}/{metric}/power with a PowerInstant payload. | Publishes validate against the schema; metric is from the battery subset of the metric enum. | All | Live
Battery telemetry | BT-2 | State telemetry shape | Battery state telemetry (SoC, etc.) publishes on dt/{siteId}/{gatewayId}/{metric}/state with a BatteryStateValue payload. | Publishes validate against the schema. | All | Live
Battery telemetry | BT-3 | Telemetry cadence | Telemetry is published at the cadence documented by Tensor (typically minutely for power and state). | Observed cadence matches documented expectation across a representative window of at least 1 hour of continuous operation. | All | Live
Battery telemetry | BT-4 | Telemetry freshness on reconnect | After a disconnect, the EMS prioritizes the latest sample over backfilled history when publishing resumes. | First message published after reconnect carries the freshest sample, not the oldest buffered one. | All | Live
Battery telemetry | BT-5 | Telemetry feedback consumption | EMS subscribes to ack-dt/{siteId}/{gatewayId} and reacts to TelemetryFeedback messages. | EMS handles status: ok and status: error feedback. | All | Live
Battery telemetry | BT-6 | Telemetry feedback retry behavior | EMS has a documented retry / drop policy in response to telemetry feedback errors. | EMS behavior matches the documented policy. | All | Live
Battery telemetry | BT-7 | TelemetryFeedback conditional fields | TelemetryFeedback carries code and detail when status is error, omits code, detail and topic when ok. Schema enforces via if/then/else. | EMS-side parser handles both shapes (no crash, no silent drop) and treats code/detail/topic on ok as a protocol violation. | All | Live
Battery telemetry | BT-8 | Malformed telemetry feedback | When Tensor Cloud cannot parse a telemetry message it acks with code: MESSAGE_MALFORMED, correlation_id: unknown (message_id unrecoverable) and a topic naming the channel. correlation_id is not constrained to the msg_ UUID pattern. | EMS parser accepts correlation_id: unknown without rejecting or dropping the feedback, and surfaces topic so an operator can identify which published message was rejected. | All | Live
Energy reporting | EN-1 | At least one energy reading stream per required metric | For each energy-flow metric required by the project type, EMS emits either a windowed stream, a lifetime counter, or both. | Every required energy-flow metric has at least one active stream across at least 1 hour of continuous operation. | All | Live
Energy reporting | EN-2 | Lifetime counter monotonicity | Values on dt/{siteId}/{gatewayId}/{metric}/lifetime never decrease across messages (except for documented counter-reset events). | Monotonic non-decreasing across a representative observation window. | All | Live
Energy reporting | EN-3 | Lifetime counter units | Lifetime payloads use kWh per EnergyLifetime schema. | All lifetime values are kWh. | All | Live
Energy reporting | EN-4 | Windowed bucket boundaries | For dt/{siteId}/{gatewayId}/{metric}/energy/{window}, start_ts and end_ts boundaries match the {window} parameter, an ISO-8601 duration (PT5M, PT30M, PT1H, etc.). | Every windowed payload's start_ts/end_ts matches the window length implied by the topic. | All | Live
Energy reporting | EN-5 | Late-arrival policy | EMS publishes windowed energy values only after the window has closed. Tensor Cloud has no late-arrival cutoff. | EMS publishes windowed values strictly after window close. Late-arriving samples are still published rather than dropped. | All | Live
Alerts | A-1 | alertEvent emission | Transient alert events publish on dt/{siteId}/{gatewayId}/alert conforming to AlertEvent. | Every emitted code is a member of AlertCode. | All | Live
Alerts | A-2 | alertState clearing semantics | When an alert resolves, the next alertState snapshot omits it. alertState is a periodic full snapshot (at least every 10 minutes, and at startup). | After a resolved alert, the next alertState does not include the resolved alert. | All | Live
Alerts | A-4 | AlertCode enumeration coverage | All codes emitted by the EMS appear in the schema's AlertCode enum. | No proprietary alert codes are emitted on these topics. | All | Live
Alerts | A-5 | alertState snapshot with no active alerts | Observe the alertState topic over a period during which no alert is firing. The snapshot is published on its normal schedule regardless of whether anything is active. | alertState continues to publish at least every 10 minutes with an empty measurement_value array. The EMS does not suppress the publish when there is nothing to report. | All | Live
Alerts | A-6 | Shared-hardware faults raise every applicable code | Applies to sites with co-located PV and battery. On a DC-linked system, simulate a fault in hardware the PV array and the battery share (hybrid inverter, common power conditioning subsystem, or common control or aggregation unit). On any topology where the EMS reaches both subsystems through a single collector device, simulate a loss of communication with that collector. | The shared-hardware fault raises both PV_OTHER and BATT_OTHER, and clearing it emits a cleared alertEvent for both. Where the EMS has no per-BMS or per-PVPCS communication visibility, collector communication loss raising both BATT_COMM_FAIL and PV_COMM_FAIL is accepted; where it does have per-device visibility, only the codes for genuinely unreachable devices are raised. | AC-link, DC-link with PV | Integrator test
Backfill | BF-1 | Reconnect replay ordering | After a network outage, the EMS resumes publishing live samples first. Only when no live sample is waiting does it replay buffered history. | Live samples ahead of backfill; backfill yields to fresh live samples whenever they arrive. | All | Live
Backfill | BF-2 | Maximum backlog age | EMS retains telemetry locally for up to 7 days. Older buffered samples are dropped or summarized. | EMS drops or summarizes buffered samples older than 7 days; samples younger than 7 days are replayed. | All | Live
Backfill | BF-3 | Duplicate handling on reconnect | When the EMS resends a sample, it reuses the same message_id as the original. Tensor Cloud dedups on message_id. | Every resend carries the same message_id as its first publish attempt. | All | Live
Batched telemetry | BA-1 | Batching mode compliance | Batching is enabled per site and is backfill-only by default. Live readings are batched only where live batching is granted, and a live batch then spans at most 60 seconds. Sites needing 1-second arrival, such as low-voltage VPP batteries, send live readings as single messages. | On a backfill-only site, every live reading is a single message and only backfill uses the batch topics. On a live-enabled site, no live batch spans more than 60 seconds. | Batch topics | Live
Batched telemetry | BA-2 | Batch payload shape and ordering | Each batch states unit, aggregation, aggregation_window and pre_qualification once, and each measurements entry carries its own message_id, measurement_ts and value. Entries are strictly ascending with unique timestamps and unique message_id, none equal to the batch's own. Gaps are absent entries, never 0 or null. | Every batch validates against PowerInstantBatch or GridFrequencyBatch; timestamps strictly ascending and unique; message_id unique within the batch and distinct from the envelope's; gaps appear as absent entries. | Batch topics | Live
Batched telemetry | BA-3 | Split on header change | The EMS starts a new batch whenever unit, aggregation, aggregation_window or pre_qualification changes. A batch never straddles entering or leaving pre-qualification test mode. | No batch contains readings taken under different header values; entering or leaving pre-qualification mode always begins a new batch. | Batch topics | Live
Batched telemetry | BA-4 | Batch size limits | A batch carries at most 900 entries and at most 122,880 encoded UTF-8 bytes. The EMS measures the serialized payload and splits before publishing rather than relying on entry count alone. | No published batch exceeds 900 entries or 122,880 encoded bytes; a series exceeding either limit is split. | Batch topics | Live
Batched telemetry | BA-5 | QoS and RETAIN on batch topics | Batch topics are published at QoS 1 and never with the MQTT RETAIN flag set. | Every publish to a batch topic uses QoS 1 with RETAIN unset. | Batch topics | Live
Batched telemetry | BA-6 | Deduplication and all-or-nothing resend | Dedup keys on each entry's message_id, not the batch's. Resends reuse the original message_id and may re-group into different batches or use the single-message form. Because a batch is accepted or rejected in full, an error means every reading in it is unstored and the whole batch is resent once corrected. | A resent reading carries the same message_id as its first publish attempt in either form; re-grouping produces no duplicate stored values; after a rejected batch the EMS resends all of its readings, not only the offending one. | Batch topics | Live
Arbitrage | AR-1 | Receive power command | EMS receives a representative BatteryPowerCommand. | Message delivered, parsed without error. | Arbitrage | Live
Arbitrage | AR-2 | Command shape per schema | Payload contains schema_version, message_id, issue_ts, res_topic, and a control object with priority (optional) and schedule (required). | Payload validates against BatteryPowerCommand. | Arbitrage | Live
Arbitrage | AR-3 | ack-cmd success response | EMS publishes on ack-cmd/{siteId} with status: ok, command_id equal to the command's message_id, and schema_version: 2.9.0. | Response validates against CommandResponse; errors is absent. | Arbitrage | Live
Arbitrage | AR-4 | ack-cmd error response shape | On rejecting a command, EMS publishes status: error with an errors array. Each error has code (from ErrorCode) and detail. | Response uses detail for each error; every code is from ErrorCode. | Arbitrage | Integrator test
Arbitrage | AR-5 | errors conditional on status | errors array present (>= 1 item) when status is error; absent when status is ok. Schema enforces via if/then/else. | errors present on error; errors absent on ok. | Arbitrage | Live + integrator test
Arbitrage | AR-6 | ErrorCode mapping | EMS uses the documented ErrorCode for each failure class: MESSAGE_MALFORMED, MISSING_FIELD, TYPE_MISMATCH, FIELD_OUT_OF_RANGE, TIME_WINDOW_INVALID, EXPIRED, DUPLICATE, RESOURCE_UNAVAILABLE, INTERNAL_ERROR. | Same failure class always produces the same code across runs. | Arbitrage | Integrator test
Arbitrage | AR-7 | Schedule gaps | Send a schedule with a time gap between intervals. During the gap, EMS falls back to any previously valid command. If none, power_kw = 0 (standby). | Gap behavior matches: fallback to previous schedule, then standby. | Arbitrage | Live
Arbitrage | AR-8 | Overlaps within a command | Send a schedule whose intervals overlap each other. | EMS rejects with a documented ErrorCode and field_path: control.schedule. | Arbitrage | Integrator test
Arbitrage | AR-9 | Empty schedule | Send a command with an empty schedule array. Schema enforces minItems: 1. | EMS rejects with a documented ErrorCode and field_path: control.schedule. | Arbitrage | Integrator test
Arbitrage | AR-10 | Priority and issue_ts tie-breaking | Different priority: higher wins. Same priority: later issue_ts wins. Same priority and issue_ts: last-received wins. | EMS executes the winning command for each tie-break scenario and acknowledges all commands. | Arbitrage | Live + integrator test
Arbitrage | AR-11 | Stale-schedule rejection | Send a command whose schedule's last interval end_ts is in the past. | EMS rejects with a documented ErrorCode. Old issue_ts alone is not a rejection reason. | Arbitrage | Integrator test
Arbitrage | AR-12 | Per-slot supersession | Send a command that overlaps only part of an in-progress schedule. The new command replaces existing schedule only for overlapping slots. | EMS uses new command's setpoints for overlapping slots; continues older command for non-overlapping slots. | Arbitrage | Live
Arbitrage | AR-13 | Mid-slot command (immediate execution) | Send a command whose first interval has a start_ts in the past and an end_ts in the future - the covered slot has already started. | EMS accepts the command and applies the active interval's setpoint immediately, without waiting for a future start time. Only a schedule whose final end_ts is also in the past is rejected as stale (see AR-11). | Arbitrage | Live
Arbitrage | AR-14 | No schedule (standby fallback) | Reach a point in time that no command covers and to which no previously valid command applies. | EMS stops the battery and holds power_kw = 0 (standby), neither charging nor discharging, until a command covering that time arrives. | Arbitrage | Live
Arbitrage | AR-15 | Mixed valid and invalid schedule items | Send a BatteryPowerCommand whose control.schedule contains both well-formed items and at least one invalid item (for example item 0 with an out-of-range power_kw, item 1 with end_ts before start_ts, and items 2 and 3 entirely valid). FCR integrators run the equivalent test for FCR commands as FC-10. | EMS applies none of the items in the command, including the valid ones, and continues executing the previously valid schedule. It responds with status error carrying one errors[] entry per invalid item, each with its own field_path, rather than stopping at the first failure. Inspecting the EMS's stored schedule after the rejection shows no trace of the command. | Arbitrage | Integrator test
Arbitrage | AR-16 | reference_point interpretation | Send a schedule whose intervals mix reference_point values, and run it while co-located generation is active. Include an interval with battery, one with grid, and one omitting the field. | On battery intervals the battery itself tracks power_kw and generation exports untouched, so a 0 interval leaves the battery idle while the site still exports. On grid intervals the metering point tracks power_kw, so a 0 interval holds the meter at zero with the battery absorbing whatever is generated. An interval omitting the field behaves identically to battery. On a DC-coupled system the EMS compensates its inverter setpoint against measured PV to achieve the battery intervals rather than passing power_kw straight through. | Arbitrage | Live
Arbitrage | AR-17 | Unreachable setpoint clamps and alerts | Drive the EMS into a setpoint it cannot deliver: a battery interval whose value plus concurrent generation exceeds the inverter rating, or a grid interval that would require charging past a full battery or discharging past an empty one. | EMS applies the closest physically achievable value, keeps executing the schedule, and raises SETPOINT_UNREACHABLE naming the limit it hit. It does not reject the command, does not respond with status error, and does not stop the battery. The alert clears once the EMS is tracking the commanded value again. | Arbitrage | Integrator test
FCR | FC-1 | Receive FCR command | EMS receives a representative BatteryFcrCommand. | Message delivered, parsed without error. | FCR | Live
FCR | FC-2 | action defaults to execute | When action is absent on a schedule item, EMS treats it as execute. | Matches the schema's default. | FCR | Live
FCR | FC-3 | capacity_kw required for execute | For action: execute (the default), EMS requires capacity_kw and rejects items missing it. Schema enforces via if/then/else. | EMS rejects with a documented ErrorCode and field_path pointing at the offending item. | FCR | Integrator test
FCR | FC-4 | capacity_kw forbidden on cancel | For action: cancel, capacity_kw is forbidden on schedule items. Schema enforces via if/then/else. | EMS rejects a cancel command carrying capacity_kw with a documented ErrorCode. | FCR | Integrator test
FCR | FC-5 | FCR Assessment II power telemetry | For every FCR-awarded slot, EMS publishes 1-second-resolution supplied power at 1 Hz on dt/{siteId}/{gatewayId}/{metric}/power (PowerInstant), PT1S-averaged with measurement_ts at the start of each whole second. Metric set matches the TSO registration: meter_export_ac/meter_import_ac (grid-connection-point) or battery_discharge_ac/battery_charge_ac (equipment-point). | Power samples arrive at 1 Hz on the registered metric(s), carry aggregation: average with aggregation_window: PT1S and whole-second measurement_ts, and time-align with the FC-8 frequency samples. | FCR | Live
FCR | FC-7 | FCR baseline composition with arbitrage | Arbitrage and FCR compose: FCR sets capacity, concurrent BatteryPowerCommand shifts baseline. | When both schedules cover the same slot, EMS applies arbitrage value as baseline and uses FCR capacity for frequency response on top. | FCR | Live
FCR | FC-8 | Grid frequency telemetry | For every FCR-awarded slot, EMS publishes grid frequency at 1 Hz on dt/{siteId}/{gatewayId}/frequency (GridFrequency), in Hz, measured at the grid connection point from the live AC waveform to >= 0.01 Hz resolution, as a PT1S average time-aligned with the 1 Hz power samples. | Frequency samples arrive at 1 Hz, carry unit: Hz and realistic values, and share measurement_ts boundaries with the power samples. | FCR | Live
FCR | FC-9 | Pre-qualification (事前審査) flag | While the EMS operator has the site in FCR pre-qualification (事前審査) test mode, EMS sets pre_qualification: true on every */power and */frequency message, and omits it (or sets false) during normal operation. | In a simulated pre-qualification run, pre_qualification: true is present on all */power and */frequency messages for the test window and absent during normal operation. | FCR | Live
FCR | FC-10 | Mixed valid and invalid schedule items (FCR) | Send a BatteryFcrCommand whose control.schedule contains both well-formed items and at least one invalid item, and run it twice. On the action execute run, make item 0 invalid with an out-of-range capacity_kw and item 1 invalid with end_ts before start_ts, leaving items 2 and 3 valid (each carrying a capacity_kw). On the action cancel run, capacity_kw is forbidden on every item, so make item 0 invalid by including one at all and item 1 invalid with end_ts before start_ts, leaving items 2 and 3 as valid time ranges with no capacity_kw. This is the FCR counterpart of AR-15; all-or-nothing validation is a protocol-wide rule, not an arbitrage-only one. | EMS applies none of the items in the command, including the valid ones, and continues executing the previously valid FCR schedule. It responds with status error carrying one errors[] entry per invalid item, each with its own field_path. For the cancel case, nothing is cancelled: every offer the command named remains in force. | FCR | Integrator test
Solar | SO-1 | Irradiation telemetry | EMS publishes on dt/{siteId}/{gatewayId}/irradiation conforming to Irradiation. | Publishes validate against the schema. | AC-link, DC-link with PV | Live
Solar | SO-2 | Irradiation cadence | EMS publishes irradiation at the documented cadence (typically continuous during daylight, paused or zero at night). | Observed cadence matches documented expectation across at least 1 hour of continuous daylight operation. | AC-link, DC-link with PV | Live
Solar | SO-3 | Curtailment reporting | EMS publishes curtailment on dt/{siteId}/{gatewayId}/curtailment conforming to Curtailment. | Publishes validate against the schema; curtailment is reported whenever the inverter is operating below available irradiation. | AC-link, DC-link with PV | Live
Solar | SO-4 | Solar power telemetry metrics | PV-related metrics (solar_to_grid_ac, solar_to_battery_ac etc.) publish on the power topic. | Every PV metric the EMS supports is emitted on dt/{siteId}/{gatewayId}/{metric}/power. | AC-link, DC-link with PV | Live
Solar | SO-5 | inverter_net_output_ac definition | EMS emits inverter_net_output_ac as the total AC-side output of the inverter, equal to inverter_to_load_ac + inverter_to_grid_ac. Values are non-negative. | Emitted values are >= 0 and equal inverter_to_load_ac + inverter_to_grid_ac. | AC-link, DC-link with PV | Live
Solar | SO-6 | Solar DC voltage and current (DC-link) | DC-link integrators publish PV-array DC voltage and current on dt/{siteId}/{gatewayId}/solar conforming to SolarDcElectrical. measurement_value carries voltage (V) and current (A), each value >= 0, as a single aggregate across the whole array measured at the DC link upstream of the inverter. Voltage and current share one measurement_ts and are published at 1-minute resolution. | Publishes validate against the schema; each message carries both voltage and current at a single measurement_ts; cadence is at least once per minute during daylight. AC-link and stand-alone integrators do not publish this channel. | DC-link with PV | Live
Site load | SL-1 | Load power telemetry | EMS publishes load-side power metrics on dt/{siteId}/{gatewayId}/{metric}/power. | Publishes validate against PowerInstant. | AC-link with load | Live
Site load | SL-2 | Load metric naming | EMS uses inverter_to_load_ac, not inverter_to_load_kwh. | Every load-related metric is the canonical name from the metric enum. | AC-link with load | Live
Site load | SL-3 | Grid-charging metric (DC-link) | For DC-link sites where grid charging is possible, EMS emits grid_to_inverter_ac. | Metric is emitted whenever the site can be charged from grid. | DC-link with grid charging | Live
Site load | SL-4 | Grid-charging metric (AC-link) | For AC-link sites where grid charging is possible, EMS emits grid_to_battery_ac. | grid_to_battery_ac is emitted whenever the site can be charged from grid. | AC-link with grid charging | Live
Project-type constraints | PT-S | Standalone metric set | EMS publishes only metrics from the required + permitted set for standalone batteries. Curtailment is still required, since a standalone battery can be subject to TSO output control even with no solar on site; irradiation is the one solar-linked channel that does not apply. | AWS IoT Core enforces topic scoping at the broker layer based on the gateway's certificate; unauthorized metric topics are rejected at connection time. | Standalone | Live
Project-type constraints | PT-AC | AC-link metric set | EMS publishes only AC-link required + permitted metrics; no DC-link-only metrics. | Only AC-link required and permitted metrics appear on any telemetry topic. | AC-link | Live
Project-type constraints | PT-DC | DC-link metric set | EMS publishes only DC-link required + permitted metrics; no AC-link-only metrics. Includes grid_to_inverter_ac when grid charging is possible. | Only DC-link required and permitted metrics appear on any telemetry topic. | DC-link | Live